ISSN: 2278-2540 | DOI: 10.51583/IJLTEMAS Committed to Quality Research and Publications Since 2012

International Journal of Latest Technology in Engineering, Management & Applied Science (IJLTEMAS)

# A Study On Details Of D.I. (Ductile Iron) Pipes

1 Jayraj B Solanki, 2 Dr. D. M. Patel, 3 Rahul S Shah

1B.E. Student, 2Principal, 3Asst. Professor

1Civil Engineering Department

1,2,3 D.A Degree Engineering & Technology, Mahemdabad-387130, Gujarat, India

Abstract: Water is a basic need of human being used for everywhere and for everything of regular life at each and every day and the routine life. For drinking and potable water purpose the rural and urban area there is work of the carrying and supplying of water there is compulsory need is laying of water carrying pipelines at each and every area of the state or city. For the purpose of carrying water to the household there is kind of work is done that called water distribution network. For the work pipe is the main part of the water distribution work. The main objective of this paper is to study the D.I Pipe used on construction sites of Morbi Municipal Corporation, Morbi there is know the Purpose and usage of the pipes.

Keywords : D.I. K-7 pipes, Diameter of pipes, Rubber Gasket, Tolerance, Coating, Testing.

.

#### INTRODUCTION

Supply of Pipe is a system that provide by contractor for the distribution of water into the area discoverd. Properties : Discussion on high tensile strength, durability, and corrosion resistance.

Focus on the supply chain, from the manufacturing unit to the project site. Quality standards & Technical Specifications

Manufacturing Standards: Emphasis on IS 8329:2000 and different classes (K7, K9).

Quality Checks: Detailed explanation of Hydrostatic tests, Lining inspections (Cement Mortar), and External coating (Zinc/Bitumen). Inventory Management: How stock is categorized based on Nominal Diameter (DN).

#### Objectives (Description)

#### For 80 mm to 450 mm Diameter

This item includes:

Note: Wherever International Standards or Indian standards / specifications are mentioned, their equivalent or higher standards / specifications are also acceptable Supply and Delivery of Ductile Iron Pipe as per IS:8329-2000 or its latest revision or amendments if any including jointing material as EPDM ring as per IS 5382- 1985 and ISO: 4633-1996 or its latest revision or amendments if any Standards.

The following standards, specifications and codes are part of this specification. In all cases, the latest revision of the including all applicable official amendments and revisions shall be referred to. In case of discrepancy between this specification and those referred to herein, this specification shall govern.

  - ISO: 10803-1997 Design method for ductile iron pipes ✓ IS:8329-2000 Centrifugally Cast (spun) ductile iron pressure pipes for water, gas and sewage

  - ISO:2531-1991 Ductile iron pipes, fittings and accessories for pressure pipelines.

  - ISO:4179-1985 Ductile iron pipes for pressure and non pressure-Centrifugal

  - cement mortar lining - General requirements.

  - IS:8112 Specification for 43 Grade ordinary Portland cement.

  - BS:3416 Bitumen based coatings for cold application, suitable for use in contact with potable water.

  - ISO:8179-1995 Ductile iron pipes-External coating- Part-1 Metallic Zinc with finishing layer.

  - IS:638 Sheet rubber jointing and rubber insertion jointing.

  - ISO:4633-1996 Rubber seals-Joint rings.

  - IS:5382-1985 Specification for Rubbe sealing rings for gas mains, water ✓ mains and sewers.

  - AWWA C600 Installation of ductile iron water mains and their appurtenances.

- Internal Diameter:

The nominal values of the internal diameters of pipe, expressed in millimeters are approximately equal to the number indicating their nominal sizes DN.

- Length:

The working length of socket and spigot pipes shall be 5 m, 5.5 m, or 6 metres.

- Thickness:

The wall thickness of pipe 'e' in mm shall be calculated as a function of the nominal diameter by the following equation with minimum of 5 mm e = K(0.5 + 0.001 DN) where : e = wall thickness in mm, DN = the nominal diameter, K = the whole number coefficient

EPDM Rubber Gasket:

Rubber Gasket shall be suitably for Push-on-Joint. Tolerances on External Diameter:

The nominal external diameter (DE) of the spigot end of socket and spigot pipes and when measured circumferentially using a diameter tape shall confirm to the requirements specified as follow. The positive tolerance is +1 mm and applies to all thickness classes of pipes. The maximum negative tolerance of the external diameter are specified as follow:

| DN | Nominal | Positive Tolerance | Negative Tolerance |
| --- | --- | --- | --- |
| 80 | 98 | +1 | -2.2 |
| 100 | 11 | +1 | -2.8 |
| 125 | 14 | +1 | -2.8 |
| 150 | 17 | +1 | -2.9 |
| 200 | 22 | +1 | -3.0 |
| 250 | 27 | +1 | -3.1 |
| 300 | 32 | +1 | -3.3 |
| 350 | 37 | +1 | -3.4 |
| 400 | 42 | +1 | -3.5 |
| 450 | 48 | +1 | -3.6 |
| 500 | 53 | +1 | -3.8 |
| 600 | 63 | +1 | -4.0 |

### Coating

Pipe shall be delivered internally and externally coated.

External Coating: Pipe shall be metallic zinc coated and after that it shall be given a finishing layer of bituminous paint as per IS - 8329-2000 Zinc coating shall comply with IS:8329/EN 545/ ISO

8179. Only molten zinc spray coating shall be acceptable. The average mass of sprayed metal shall not be less than 130 g/sqm with a local minimum of 110 g/sqm.

Bitumen overcoat shall be of normal thickness of 70 microns unless otherwise specified. It shall be a cold applied compound complying with the requirements of BS 3416 Type II suitable for tropical climates factory applied preferably through an automatic process. Damaged areas of coating shall be repainted on

site after removing any remaining loose coating and wire brushing any rusted areas of pipe.

Internal lining: Internally pipe shall be Portland Cement mortar lined (as per IS - 8329-2000). The mortar shall contain by mass at least one part of cement to 3.5 part of san All pipes and fittings shall be internally lined with cement mortar using high speed centrifugal process in accordance with IWO 4179/IS 8329. Cement mortar lining shall be applied at the pipe manufacturing shop in conformity with the aforesaid standards. No admixtures n the mortar shall be used without the approval of the Engineer. The sand to cement proportion of sand if justified by the sieve analysis.

### Joint

Jointing of DI pipes and fittings shall be push-on type Push-on-joints The Contractor shall source the push-on-joint gaskets only from the pipe manufactures. In turn the pipe manufacturer shall supply at least 10% additional quantity of gaskets over and above the requirement to the Contractor at no extra cost.

Rubber ring bundles form every lot shall carry with them manufacturers test certificate for the following mechanical properties.

1. Hardness 2. Tensile strength 3. Compression test 4. Accelerated again test 5. Water absorption test

6. Stress relaxation test

Rubber rings shall be clearly labeled in bundles to indicate the type of ring, the type of joint, the size of the pipe with which they are to be used, the manufacturer’s name and trade mark, the month and year of manufacture and the shelf life.

### Testing of Pipe:

The main test among others to be conducted shall be as per IS:8329-2000 or with its latest revision/amendments.

- Mechanical Tests

Mechanical tests shall be carried out during manufacture of pipes as specified in the Standards. The frequency and sampling of tests for each batch of pipes shall be in accordance with IS 11606-1986. The test results so obtained for all the pipes and fittings of different sizes shall be submitted to Engineer. The method for tensile tests and the minimum tensile strength requirement for pipes and fittings shall be as per IS;8329/EN 545 for pipes and IS:9523/EN 545 for fittings.

- Brinell Hardness Test

For checking the Brinell hardness the test shall be carried out on the test ring or bars cut from the pipes used for the ring test and tensile test in accordance with IS:1500. The test shall comply with the requirements specified in IS:1500/ISO 6506. [c] Re-tests If any test piece representing a lot fails in the first instance, two additional tests shall be made on test pieces selected from two other pipes from the same lot. If both the test results satisfy the specified requirements the lot shall be accepted Should either of these additional test pieces fall to pass the test, the lot shall be liable for rejection.

- Flow Test shall be done in two stage;

#### Stage 1

Pipe line shall be laid by resting the pipe line on supports at joints. The pipeline and all joints of pipes shall be made thoroughly sound and water tight and any joint which may be observed to be leaky shall be immediately corrected. Thus after satisfactory flow test sand bedding shall be fill pipe line after laying pipe line. The refilling of trench shall be carried out then after.

#### Stage 2

After total laying & refilling of trenches, flow test shall be carried out again for particular section of length as suggested by engineer in charge.

### Quality Assurance

The manufacturer shall have a laid down Quality Assurance Plan for the manufacture of the products offered which shall be submitted along with the tenders.

#### MARKING :

The methods of marking all the pipes to be delivered under scope of contract shall ensure that all the information will remain legible even after transportation, storage in open space etc. In general the legible and indelible marking upon the goods shall indicate the followings;

- Certification mark on each pipe.

- Manufacturers brand name and/or trademark.

- Purchasers mark as “MMC” be inscribe

- The outside diameter and pressure rating.

- Batch number or lot number.

- Inspector’s mark on each pipe

### INSPECTION

Inspection of pipes and specials will be carried out by Executive engineer or his representative agency appointed by MMC. All the expenditure for inspection shall be borne by the contractor except inspection charges if any in case of inspection agency appointed by MMC shall be paid by MMC.

### ACKNOWLEDGMENT

I take this opportunity to thank all those who have contributed in successful completion of this work. I would like to thank my Guide, Mr. RAHUL SHAH Sir & Principal Sir for their full support, expert guidance & encouragement throughout the work.

### REFERENCES

- Primary Standard: IS 8329:2000 (Centrifugally Cast Ductile Iron Pressure Pipes for Water, Gas, and Sewage).

- IS 8329 (Annexure) – Covers the internal Cement Mortar Lining.

- ISO 8179 – Often referenced alongside Indian standards for External Zinc Coating.

- IS 15085 – Standards for Polyethylene Sleeving (used in highly corrosive soils to wrap the pipe).

- Vishipara WDS Tender Copy